****

***Technical Assistance:*** *800-257-5911 or 215-766-2670*

***Email:***[*info@scaletronscales.com*](mailto:info@scaletronscales.com)

***Website:***[*www.scaletronscales.com/downloads*](https://www.scaletronscales.com/downloads/)

**TYPICAL SPECIFICATION FOR MODEL 2305D™ ECONOMICAL DIGITAL DUAL CYLINDER SCALE WITH ACCUPRO 6000-TS CONTROLLER**

**SCALE PLATFORM**

**Capacity:** A quantity of \_\_\_\_\_\_ Economical Digital Dual Cylinder Scale(s) shall be provided for weighing two (2) 150 lb. gas cylinders independently. Scale shall be of the digital readout/electronic load cell type with a net capacity of 150 lbs. (68 or 70 kg) for each base. Scale base shall be of the single load cell design.

**Platform:** Scale platforms shall each be sized to accept one (1) 150 lb. cylinder up to 12" (304.8 mm) in diameter. Scale must have a rugged, steel frame that is protected by a corrosion resistant coating. Coating system shall consist of a zinc oxide primer and dry powder epoxy that is resistant to chemicals, moisture and UV light. The decking shall be solid, 1/4" thick PVC to protect scale base from abrasion. All hardware shall be stainless steel. The platform height shall not exceed 1.56" (40 mm) so as not to require a pit or ramp. A stainless steel leveling foot shall be supplied with the load cell. A heavy-duty adjustable backstop shall be provided to facilitate centering of cylinders on the platform. There must be a provision for securing weigh frame to floor. A wall-mounted cylinder restraining bracket with integral tool rack shall be provided.

**Load Cell:** Weight shall be transferred via a pivoted platform to a single, NTEP approved, temperature compensated stainless steel shear beam load cell. A flexible, four (4) conductor cable with a minimum length of 12 feet shall connect load cell to controller and allow easy remote installation of the readout. Cable length shall be \_\_\_\_\_\_ ft. (12 ft. is standard).

**CONTROLLER (INDICATOR)**

**Display & Operation:** Controller must be electronic and have a 4.3" alphanumeric/graphic color LCD touch screen display with adjustable brightness and 6-digits for weight value. The controller shall give operator the ability to monitor chemical by weight or volume in pounds, kilograms, gallons or liters. A touch screen shall be provided for programming and setting tare weights. A multi-level menu system and bar graph display shall be provided for ease of operation and must be able to display the difference between net and tare weight. Controller shall offer up to eleven (11) single-channel and five (5) dual-channel weight displays and have a provision for password protection to prevent unauthorized use. Controller shall be field programmable and calibratable with no test weights.

**Channels & Set Points:** Controller shall monitor one (1) or two (2) channels. Each channel shall have available two (2) or four (4) adjustable set points in order to display low or high level conditions on the controller. Set points shall activate 3A relay contacts. Each channel shall display net and gross weight; net and gross percent (%); net and gross weight bar graphs plus mA out, tare adjustment and set point values. Ability to mix different scale types on one controller shall be standard.

**Outputs & Alarms:** Controller shall provide for each channel an adjustable 4-20 mA analog output signal, scale powered, that outputs net weight to provide the versatility to interface with related equipment. An option for remote monitoring capabilities with either Modbus TCP through ethernet or Modbus RTU via RS-232/RS-485 serial network shall also be provided.

*Page 1 of 2*

Controller shall feature both a tri-color-status light and an optional 78 dB audible piezo buzzer alarm with external buzzer support to aid operator in monitoring critical alarm and alert conditions. Controller shall sound and display an alarm or alert for both low-level and high-level conditions. A leak detector input with the ability to trigger alarms and alerts shall be standard.

**Enclosure:** Controller shall be housed in a NEMA 4X, UL approved enclosure and shall carry CE marking. Power requirement shall be 100/277 VAC. Controller shall be capable of remote mounting up to 200 ft. from scale base.

**COMPLETE SCALE**

**Accuracy & Warranty:** Accuracy shall be ±0.1% of full scale capacity, or better. Scale and controller shall carry a full five (5) year factory warranty. “Limited” warranties shall not be accepted.

Scale shall be a Model 2305D-\_\_\_\_\_\_\_\_\_\_\_\_ with 6000-TS controller with two (2) channels and \_\_\_\_\_\_ set points as manufactured by Scaletron Industries Ltd., Plumsteadville, PA.

**PART NUMBERS**

**Platform Part Numbers**

|  |  |  |
| --- | --- | --- |
| MODEL | SIZE | NET CAPACITY |
| 2305D-150LB | 12" Diameter | 150 lbs. Per Base |
| 2305D-68 or 70KG | 12" Diameter | 68 or 70 kg Per Base |

**Controller Part Number**

|  |  |  |
| --- | --- | --- |
| 6000-TS-2 | Touch Screen | Two Channel |

**Scaletron™ Industries, Ltd.**  Toll Free: 1-800-257-5911 (USA & Canada)

Bedminster Industrial Park Phone: (+1) 215-766-2670 (International)

53 Appletree Lane Fax: (+1) 215-766-2672

P.O. Box 365 E-mail: [info@scaletronscales.com](mailto:info@scaletronscales.com)

Plumsteadville, PA 18949 USA Website: [www.scaletronscales.com](http://www.scaletronscales.com/)

*Page 2 of 2*