****

***Technical Assistance:*** *800-257-5911 or 215-766-2670*

***Email:****info@scaletronscales.com*

***Website:***[*www.scaletronscales.com/downloads*](https://www.scaletronscales.com/downloads/)

**TYPICAL SPECIFICATION FOR ACCUPRO 7000-TS™ DIGITAL SCALE CONTROLLER (INDICATOR)**

**Display & Operation:** Controller must be electronic and have a 4.3" alphanumeric/graphic color LCD touch screen display with adjustable brightness and 6-digits for weight value. The controller shall give operator the ability to monitor chemical by weight or volume in pounds, kilograms, gallons or liters. A touch screen shall be provided for programming and setting tare weights. A multi-level menu system and bar graph display shall be provided for ease of operation and must be able to display the difference between net and tare weight. Controller shall offer up to thirteen (13) single-channel and six (6)) dual-channel weight displays and have a provision for tare lock-out and password protection to prevent unauthorized use. Controller shall be field programmable and calibratable with no test weights.

**Channels & Set Points:** Controller shall monitor up to four (4) channels. Each channel shall have available two (2) or four (4) adjustable set points (maximum eight (8) total per controller) in order to display low or high level conditions on the controller. Set points shall activate 3A relay contacts. Each channel shall display net and gross weight; net and gross percent (%); net and gross weight bar graphs plus mA out, tare adjustment, set point values, on-screen and memory-stored historical data log, feed rate, daily usage, current amount used and days till empty. Ability to mix different scale types on one controller shall be standard.

**Outputs & Alarms:** Controller shall provide for each channel an adjustable 4-20 mA analog output signal, scale powered, that outputs net weight to provide the versatility to interface with related equipment. An option for remote monitoring capabilities with either Modbus TCP through ethernet or Modbus RTU via RS-232/RS-485 serial network shall also be provided. Controller shall feature both a tri-color-status light and a built-in 78 dB audible piezo buzzer alarm with external buzzer support to aid operator in monitoring critical alarm and alert conditions. Controller shall sound and display an alarm or alert for both low-level and high-level conditions. A leak detector input with the ability to trigger alarms and alerts shall be standard.

**Enclosure:** Controller shall be housed in a NEMA 4X, UL approved enclosure and shall carry CE marking. Power requirement shall be 100/277 VAC. Controller shall be capable of remote mounting up to 200 ft. from scale base.

**Accuracy & Warranty:** Accuracy shall be ±0.1% of full scale capacity, or better. Controller shall carry a full five (5) year factory warranty. “Limited” warranties shall not be accepted.

Controller shall be a Model 7000-TS-\_\_\_\_\_\_ with \_\_\_\_\_\_ channels and \_\_\_\_\_\_ set points as manufactured by Scaletron Industries Ltd., Plumsteadville, PA.

**Part Numbers**

|  |  |  |
| --- | --- | --- |
| MODEL | INTERFACE | CHANNELS |
| 7000-TS-1 | Touch Screen | One Channel |
| 7000-TS-2 | Touch Screen | Two Channel |
| 7000-TS-3 | Touch Screen | Three Channel |
| 7000-TS-4 | Touch Screen | Four Channel |

**Scaletron™ Industries, Ltd.**  Toll Free: 1-800-257-5911 (USA & Canada)

Bedminster Industrial Park Phone: (+1) 215-766-2670 (International)

53 Appletree Lane Fax: (+1) 215-766-2672

P.O. Box 365 E-mail: info@scaletronscales.com

Plumsteadville, PA 18949 USA Website: [www.scaletronscales.com](http://www.scaletronscales.com/)